## Slide 1
IEC 61400-12-1 FDIS 2016 Consensus Analysis Project
Lee Cameron
December 13, 2016

## Slide 2: Contextual Introduction
IEC 61400-12-1: “Power Performance Measurements of Electricity Producing Wind Turbines”
Last published in 2005. New issue due in beginning of 2017.
  Remote Sensing Devices
    Only met masts were allowed previously
  Rotor Equivalent Wind Speed
    To correct for the influence of shear
  Turbulence Renormalisation
    To correct for the influence of turbulence
  Many changes to the uncertainty method to reflect these changes in instrumentation and method
  Lots of other small changes
    Relative humidity influence on density, statistical uncertainty due to site calibration considered, changes to anemometer classification, etc.

## Slide 3: Power Performance Test Procedure
Notes: Data normalisation = density, turbulence and shear corrections

## Slide 4: Project Aim
In this project we aim to demonstrate the proper implementation of the new IEC power performance testing standard, with focus on the uncertainty calculation.
We aim to do this by creating a collection of Excel spreadsheet calculations for key sections.
The calculations will be modular in structure, each showing the method for a small section.

## Slide 5: Power Curve Uncertainty Calculations
Uncertainty combination
Equation E.8 in the standard gives the method for combining separate uncertainty contributions to give overall uncertainty
This is the AEP uncertainty. It is what we need to calculate!

## Slide 6: Power Curve Uncertainty Calculations
Uncertainty combination
Equation E.8 in the standard gives the method for combining separate uncertainty contributions to give overall uncertainty
Hours in a year. This turns our uncertainty in power into and uncertainty in energy

## Slide 7: Power Curve Uncertainty Calculations
Uncertainty combination
Equation E.8 in the standard gives the method for combining separate uncertainty contributions to give overall uncertainty
Many components vary with wind speed so the combination is performed across all bins of the power curve

## Slide 8: Power Curve Uncertainty Calculations
Uncertainty combination
Equation E.8 in the standard gives the method for combining separate uncertainty contributions to give overall uncertainty
Relative occurrence of each wind speed bin (to account for long term wind speed distribution)

## Slide 9: Power Curve Uncertainty Calculations
Uncertainty combination
Equation E.8 in the standard gives the method for combining separate uncertainty contributions to give overall uncertainty
Category A uncertainties
Statistical uncertainties, based on the data. Due to statistical scatter, do not account for potential bias.
Category B uncertainties
To reflect potential bias in instrumentation and due to methodology.

## Slide 10: Power Curve Uncertainty Calculations
Uncertainty combination
Equation E.8 in the standard gives the method for combining separate uncertainty contributions to give overall uncertainty
Category A uncertainties
Statistical uncertainties, based on the data. Due to statistical scatter, do not account for potential bias.
Category B uncertainties
To reflect potential bias in instrumentation and due to methodology.
We have a made spreadsheet demonstrating the calculation of each category A and B uncertainty component

## Slide 11: Power Curve Uncertainty Components
Category A - Power
“Power Curve Measurement Using The Method of Bins.xlsx”
Simple and well understood
  Related to the standard deviation in each power curve bin

## Slide 12: Power Curve Uncertainty Components
Category A - Site Calibration
“Site Calibration Using Linear Regression.xlsx”
New in this issue of the standard
Based on “K-Fold Analysis”:
  Break the site calibration filtered dataset into 10 subsets (“folds”)
  Predict turbine mast wind speed for each subset using the calibration data from the other 9 folds
  Uncertainty is based on the standard deviation of prediction error in each fold

## Slide 13: Power Curve Uncertainty Components
Category B - Power
“E.5 Category B Uncertainty in Electric Power.xlsx”
Uncertainties due to:
  Current and voltage transformers
  Power transducer
  Data acquisition
Depends on the classification of voltage and current transformers
  IEC 60044-1 gives uncertainties for different class of current transformers
  IEC 60688-1 gives uncertainties for different class power transducers

## Slide 14: Power Curve Uncertainty Components
Category B – Wind Speed
“due to hardware used”, i.e. WS measurement instrumentation
For cup or sonic anemometer:
Components due to:
Pre-test calibration,
Post-test calibration
Classification
Mounting
Lightning Finial
Data acquisition system
Notes: REWS is not a piece of hardware, rather it is a definition of wind speed measurement. You can measure this using either mast or RSD in theory, although only RSD is practical.

## Slide 15: Power Curve Uncertainty Components
Category B – Wind Speed
“due to hardware used”, i.e. WS measurement instrumentation
For RSD:
Components due to:
Verification test vs mast
In-situ comparison to mast
RSD classification
Mounting
Flow variation in the measurement volume
Monitoring of the RSD
Notes: REWS is not a piece of hardware, rather it is a definition of wind speed measurement. You can measure this using either mast or RSD in theory, although only RSD is practical.

## Slide 16: Power Curve Uncertainty Components
Category B – Wind Speed
"E.13.3 Category B Uncertainty in the Wind Speed Measurement.xlsx"
Uncertainties due to:
  Hardware used
    "E.13.4 Category B uncertainty in wind speed from cup or sonic.xlsx"
    "E.13.5 Category B uncertainty in wind speed from RSD.xlsx"
    "E.13.6 Category B uncertainty in wind speed from REWS.xlsx"
  Terrain
    "E.13.11 Category B uncertainty in wind speed from flow distortion due to terrain.xlsx“
    Related to the site calibration (or lack thereof)
  Air Density Correction
    "E.10 Category B uncertainty in Air Density.xlsx"
    Related to air density correction
Notes: REWS is not a piece of hardware, rather it is a definition of wind speed measurement. You can measure this using either mast or RSD in theory, although only RSD is practical.

## Slide 17: Power Curve Uncertainty Components
Category B – Temperature, Pressure and Relative Humidity
"E.10 Category B uncertainty in Air Density.xlsx"
Relative humidity was not included in the previous standard
Same components, but sensitivity factor has changed in this issue of the standard
All informed by manufacturer specs with extra penalties if measurement is far from hub height
Temperature:
Calibration
Shielding
Mounting
Data acquisition
Relative Humidity:
Calibration
Mounting
Data acquisition
Pressure:
Calibration
Mounting
Data acquisition

## Slide 18: Power Curve Uncertainty Components
Category B – Method related components
"E.13.15 Category B Uncertainty Calculation for Method related components.xlsx"
Many new sub-components in this issue of the standard
Uncertainties due to:
  Uncertainty in calculation of wind shear & veer
  Uncertainty due to lack of knowledge of upflow angle & turbulence
  Uncertainty due to unquantifiable seasonal effects
  Uncertainty due to cold climate
  Uncertainty due to turbulence normalisation

## Slide 19: Power Performance Analysis Procedure

## Slide 20: PCWG Feedback
The worked examples have been shared with group members via the PCWG DropBox
A number of issues were pointed out:
  Some issues with combination of uncertainties in “E.2 Combining Uncertainties.xlslx”
  Further clarification/commentary on some aspects of the methodology
  Coverage factor to apply calibration certificates (k=1 for consistency with other uncertainty components)
  Other small errors in formulae and captions

## Slide 21: PCWG Feedback
These issues are being addressed and version 2 of the spreadsheets will be added to the DropBox for final review by PCWG members soon
They will then be open-sourced via the PCWG website

## Slide 22
REFERENCES
[1] Lawrence, A., (2016), Power Curve Measurement Using Method of Bins, RES CALCULATION, TC01-037758, Issue 01
[2] Lawrence, A., (2016), Site Calibration Using Linear Regression, RES CALCULATION, TC01-038042, Issue 01
[3] Cameron, L., (2016), E.2 Combining Uncertainties, RES CALCULATION, TC01-037849, Issue 01
[4] Lawrence, A., (2016), E.5 Category B Uncertainty in Electric Power, RES CALCULATION, TC01-037769, Issue 01
[5] Cameron, L., (2016), E.13.3 Category B Uncertainty in the Wind Speed Measurement.xlsx, RES CALCULATION, TC01-037880, Issue 01
[6] Cameron, L., (2016), E.10 Category B uncertainty in Air Density, RES CALCULATION, TC01-037869, Issue 01
[7] Cameron, L., (2016), E.13.15 Category B Uncertainty Calculation for Method related components, RES CALCULATION, TC01-037863, Issue 01
[8] Cameron, L., (2016), E.13.4 Category B uncertainty in wind speed from cup or sonic, RES CALCULATION, TC01-037795, Issue 01
[9] Cameron, L., (2016), E.13.5 Category B uncertainty in wind speed from RSD, RES CALCULATION, TC01-037792, Issue 01
[10] Cameron, L., (2016), E.13.11 Category B uncertainty in wind speed from flow distortion due to terrain, RES CALCULATION, TC01-037833, Issue 01
[11] Cameron, L., (2016) E.13.6 Categiry B uncertainty in wind speed from REWS, RES CALCULATION, TC01-037812, Not yet issued

## Slide 23: Reflections
The new standard is much more complicated than the previous version
  More potential measurement setups allowed
  More sophisticated analysis methods (e.g. REWS, turbulence renormalisation)
The uncertainty annex is “informative”
  It is not a firm set of rules but gives guidance on how to perform uncertainty calculations
  Often sections are open to interpretation
RES will open source these workbooks through PCWG website to guide the industry on how to sensibly interpret the uncertainty annexes
The standard is not complete
  Some typos, incompatible units in equations etc.

## Slide 24: Presentation Contents
Power Performance Test Procedure
Power Curve Uncertainty Consensus Analyses
  Project Plan
  Uncertainty calculations
    Combination of components,
    Category A uncertainties
    Category B uncertainties
    Map of the consensus analysis workbooks
PCWG Feedback
Conclusions

## Slide 25: Simplistic Power Performance Test Procedure
Before the turbine is built, we erect two masts (or RSDs?)
  One were the turbine will be located
  One at a distance approximately 2.5 rotor diameters away
The data we collect allows us to establish a relationship in wind speed between the two locations
  This is known as the site calibration phase

## Slide 26: Simplistic Power Performance Test Procedure
Then the “turbine mast” gets knocked down, and a turbine is erected
  We can infer the turbine location wind speed from the reference mast and the site calibration relationship
The concurrent power and wind speed data (after filtering for wakes etc.) forms the power curve test dataset

## Slide 27: Simplistic Power Performance Test Procedure
The test dataset is binned by wind speed
  Normalisation such as density and turbulence correction can also be performed
The mean power in each bin is calculated to give the measured power curve
Notes: Data normalisation = density, turbulence and shear corrections

## Slide 28: Simplistic Power Performance Test Procedure
Multiply the power curve by a long term WS distribution to calculate the Annual Energy Production (AEP):
X
Notes: Data normalisation = density, turbulence and shear corrections

## Slide 29: Simplistic Power Performance Test Procedure
Calculated the uncertainty associated with the measured power curve, and hence the estimated AEP.
Is the manufacturer’s guaranteed performance being met in reality (within the uncertainty of the test)?
Notes: Data normalisation = density, turbulence and shear corrections