## Slide 1
Results from the Offshore Wind Accelerator (OWA) Power Curve Validation using LiDAR Project
Lee Cameron, Alex Clerc, Peter Stuart, Simon Feeney, Ian Couchman (FNC)
17th Meeting of the Power Curve Working Group
UL, Frankfurt, Germany
20th May 2016

## Slide 2: Contents
Project Overview
Analysis Results
  Power Curve Comparisons
  Power Curve Self-Consistency
  Sensitivity Analysis
  Correction Methods
Conclusions

## Slide 3: Project Overview
Project comprises detailed analysis of existing LiDAR based power curve datasets submitted by OWA members and RES
Datasets represent most common approaches offshore:
  Nacelle mounted LiDAR
  Transition Piece (TP) mounted scanning LiDAR
  Floating LiDAR
Technology | Datasets
Nacelle | 5 datasets in total, 4 concurrent with masts
Scanning | 2 datasets, comparable with each other, but no concurrent mast data
Floating | 2 datasets: One dataset too far from turbine One dataset too short for quantitative analysis
Dataset summary

## Slide 4
Power Curve Comparisons

## Slide 5
Comparisons to Met Masts
  Can LiDARs measure power curves that agree with mast measured power curves?
  Comparisons to IEC compliant masts carry most weight

## Slide 6: Analysis – Compare LiDAR and Mast
Cyclops Mast vs Nacelle LiDAR
Onshore
  Using only sectors where site calibration shows no speed up
Mast analysis is IEC compliant
Both measurements at 2.6D
Mean power curves in close agreement
  AEP agrees to within 0.6%
Scatter is much lower for nacelle LiDAR measurement
Measurement Device | Measurement Distance | Hours of Valid Data
Mast | 2.6D | 740
Nacelle LiDAR | 2.6D | 680
Binned power curves
Cyclops setup
AEP Comparison
Power curve scatter plot

## Slide 7: Analysis – Compare LiDAR and Mast
Rødsand 2 T73 Mast vs Nacelle LiDAR
Offshore
Mast analysis is IEC compliant
Mean power curves in close agreement
  AEP agrees to 0.1%
Scatter is lower for the nacelle LiDAR measurement
Measurement Device | Measurement Distance | Hours of Valid Data
Mast | 3.7D | 950
Nacelle LiDAR | 2.6D | 964
Binned power curves
Rødsand setup
AEP Comparison
Power curve scatter plot

## Slide 8: Analysis – Compare LiDAR and Mast
Rødsand 2 T74 Mast vs Nacelle LiDAR
Offshore
Mean power curves in close agreement
  AEP agrees to within 0.6%
Scatter is lower for the nacelle LiDAR measurement
Measurement Device | Measurement Distance | Hours of Valid Data
Mast | 8.3D | 670
Nacelle LiDAR | 2.6D | 746
Binned power curves
Rødsand setup
AEP Comparison
Power curve scatter plot

## Slide 9: Analysis – Compare LiDAR and Mast
Project L Mast vs Nacelle LiDAR
Offshore
Some disagreement (3% AEP) between mean power curves
  measurement locations differ significantly (2.5D for LiDAR, 25.0D for mast)
Scatter is significantly lower for the nacelle LiDAR measurement
Measurement Device | Measurement Distance | Hours of Valid Data
Mast | 25.0D | 438
Nacelle LiDAR | 2.5D | 457
Binned power curves
Project L setup
AEP Comparison
Power curve scatter plot

## Slide 10
LiDAR-LiDAR Comparisons
Are LiDAR power curves consistent across different turbines?

## Slide 11: Analysis – LiDAR-LiDAR Comparisons
Turbine | Measurement Distance | Hours of Valid Data
A3 | 3.5D | 1416
K3 | 3.5D | 125
Sheringham Shoal A3 TP LiDAR vs K3 TP LiDAR
Offshore
Free stream sectors do not overlap
Mean power curves in close agreement
  AEP agrees to within 0.2%
Binned power curves
Sheringham Shoal setup
AEP Comparison
Power curve scatter plot

## Slide 12
Self-consistency
Do LiDAR power curves have comparable scatter to masts?

## Slide 13: Analysis – Self-Consistency
Category A Uncertainty quantifies scatter about the mean power curve
Category A Uncertainty decreases with data count – in the above plot all uncertainties have been corrected to 700 hours valid data for comparison
More scatter
Less scatter
Onshore
Offshore
Notes: Reverse grouping for next slide  grouped by site

## Slide 14: Analysis – Self-Consistency
Promising results for SL mounted on the turbine transition piece
Note this is from one site and no comparisons to masts have been made
More scatter
Less scatter
Onshore
Offshore

## Slide 15: Analysis – Self-Consistency
  Highly precise power curve measurement for all nacelle LiDAR datasets
For each dataset where a comparison can be made, nacelle LiDAR power curve precision is superior to that achieved using masts
More scatter
Less scatter
Onshore
Offshore

## Slide 16: Analysis – Self-Consistency
  Highly precise power curve measurement for all nacelle LiDAR datasets
For each dataset where a comparison can be made, nacelle LiDAR power curve precision is superior to that achieved using masts
More scatter
Less scatter
Onshore
Offshore

## Slide 17: Analysis – Sensitivity
Power Curve Sensitivity Analysis
  What key variables are associated with variation in performance?
  Are there differences between mast and LiDAR sensitivities?

## Slide 18: Analysis – Sensitivity
Wind speed measurement is completely precise and enough to predict power with no error.
Hypothetical power curve with 0% NMAE
Notes: LiDAR tilt angle sensitivity  correlation to WS/power
Significant * significance
100% bar
Remove y-axis vals

## Slide 19: Analysis – Sensitivity
Wind speed and TI measurements are completely precise and enough to predict power with no error.
Adding deterministic variation due to TI (IEC Draft TI Renormalisation)
Notes: LiDAR tilt angle sensitivity  correlation to WS/power
Significant * significance
100% bar
Remove y-axis vals

## Slide 20: Analysis – Sensitivity
Systematic variation with TI is clearly discernible particularly in the knee region.
Binning by TI
Notes: LiDAR tilt angle sensitivity  correlation to WS/power
Significant * significance
100% bar
Remove y-axis vals

## Slide 21: Analysis – Sensitivity
Systematic variation with TI is less easy to discern; it is masked by noise.
Low power curve scatter helps the effect of environmental variables to be identified.
Adding random Gaussian noise to the wind speed signal
Notes: LiDAR tilt angle sensitivity  correlation to WS/power
Significant * significance
100% bar
Remove y-axis vals

## Slide 22: Analysis – Sensitivity
Nacelle LiDAR and masts show the same sensitivity pattern. Shear and Turbulence are the most significant factors for power curve variation.
LiDAR Tilt Angle is not associated with significant power curve variation
  Mast and LiDAR analyses show comparable variation metric (mast slightly higher). The influence is therefore thought to be due to cross correlation with other variables.
TP scanning LiDAR shows a similar sensitivity pattern but the result is based on only one test
Notes: LiDAR tilt angle sensitivity  correlation to WS/power
Significant * significance
100% bar
Remove y-axis vals

## Slide 23: Analysis – Sensitivity
Correction Methods
  TI Renormalisation
  REWS

## Slide 24: Analysis – Correction Methods
Turbulence Renormalisation
Using either LiDAR or mast sensitivity of the power curve to TI is reduced through the application of TI renormalisation for both Cyclops and Rødsand 2 T73
These results imply that TI renormalisation can be applied successfully using LiDAR measured TI signal as long as reference and measured TI are consistent

## Slide 25: Analysis – Correction Methods
REWS Analysis for Cyclops nacelle LiDAR
For the Cyclops dataset, using REWS as opposed to HHWS does not reduce the scatter (NMAE is slightly higher when using REWS).
Power curve sensitivity to shear exponent is not reduced by using the REWS for Cyclops.

## Slide 26
Conclusions

## Slide 27: Conclusions
Both nacelle and TP scanning LiDARs can be used to perform precise measurements of power curves offshore
Insufficient data to properly evaluate application of floating LiDAR to power performance measurement
For the datasets studied TI renormalisation using a nacelle LiDAR TI measurement is equally effective as mast based TI renormalisation
For Cyclops use of REWS correction does not reduce power curve scatter or power curve sensitivity to shear exponent

## Slide 28: Future Work
Future work:
  A public report will be released covering the contents of this presentation in more detail
Thank you to the Carbon Trust, OWA TWG and dataset providers!

## Slide 30
Uncertainty Discussion
Can LiDARs achieve lower uncertainty than masts?
Notes: A BIT MORE BACKGROUND – WHY DO WE CARE ABOUT UNCERTAINTY?

## Slide 31: Illustrative Uncertainties
LiDAR power curve uncertainties must always be higher than mast power curve uncertainty due to LiDAR wind speed calibration against an anemometer
Large uncertainty contribution from reference anemometer
Additional uncertainty due to pointing accuracy, horizontal vector reconstruction
Notes: REDUCE TEXT

## Slide 32: Illustrative Uncertainties
Key potential for improvement: improve the wind speed reference used in LiDAR calibration
The relatively high uncertainty assigned to LiDAR measured power curves is strange given their precision and consistently close agreement with masts
Improve WS reference?
Improved calibration procedure?
Improve WS reference?
Notes: REDUCE TEXT

## Slide 33: Uncertainty Discussion
Accurate: average of measurements is near the bullseye
Precise (Repeatable): measurements are consistent (low scatter)
Precise and Accurate
Accurate
Precise

## Slide 34: Uncertainty Discussion
A mast measured power curve is accurate but less repeatable
LiDAR gives a precise power curve, but is it accurate?
Accurate: average of measurements is near the bullseye
Precise (Repeatable): measurements are consistent (low scatter)

## Slide 35: Uncertainty Discussion
In the project, we have observed LiDARs measuring power curves with better precision and very similar accuracy to mast power curves (AEP agreement 0.1% to 0.6%)
LiDAR power curve measurements
Mast power curve measurements
However, the accuracy cannot be well defined (assigned uncertainty is large) because of the large uncertainty assigned to wind speed measurement
Can we define a better bullseye?

## Slide 36: Uncertainty Discussion
Potential solutions to reducing LiDAR wind speed uncertainty may include:
  Reduce the uncertainty of the reference anemometer (as presented by Mike Courtney*)
  Use a different instrument to measure the reference wind speed (perhaps three orthogonal lidics?)
  Define the reference speed using a spinning target?
*M. Courtney, “Why are lidars so uncertain?”, EWEA Resource Assessment Workshop, Helsinki, June 2015

## Slide 37: Uncertainty Discussion
Potential solution to reduce contractual power curve uncertainty: the Golden Turbine concept
  The golden turbine is a reference turbine which the manufacturer and the owner both have confidence in
  Use owner’s test LiDAR to measure the AEP of the “golden turbine”
  Move the test LiDAR to the test turbine and measure its performance relative to the golden turbine
  Relative performance could conceivably be measured with very low uncertainty – very useful for a contractual test!
Step 2: Test LiDAR deployed on Test Turbine
Step 1: Test LiDAR measures at Golden Turbine