## Slide 1
PCWG-Share-01 Initial Results
PCWG Meeting Kings Langley
9th December 2015
Peter Stuart (RES), Lee Cameron (RES), Alex Clerc (RES)
& Andy Clifton (NREL), on behalf of the Power Curve Working Group

## Slide 2
Download PCWG 2015 ‘A3’ Roadmap from www.pcwg.org

## Slide 3
PCWG-Share-01: PCWG Analysis Tool
Excel Benchmark and PCWG Analysis Tool Comparison
PCWG-Share-01: Enabled by PCWG Analysis Tool.
Consistent data analysis and anonymous report generation.
‘Just do it’ PCWG-Share-01 button (minimise set-up time)

## Slide 4
PCWG-Share-01 Definition Document
Download PCWG-Share-01 Definition Doc from www.pcwg.prg

## Slide 5
Inner Range Power Curves Extracted from the Dataset Itself: the data analysis process has been designed such that the warranted power curve is never considered. Instead a power curve is extracted from a subset of the data (Inner-Range) which is then used to model the power output in the outer-range.
Intelligence Sharing, not Data Sharing: the data analysis process has been designed such that the datasets do not need to be shared outside of the participant organisations. Instead of sharing the actual data, participants will share performance metrics which describe the accuracy of the trial methodologies.
PCWG-Share-01: Neutralising Commercial Sensitivities

## Slide 6
Proprietary Dataset D
Analysis Definition Y
Organization D
Proprietary Dataset A
Organization A
Proprietary Dataset B
Organization B
Proprietary Dataset C
Organization C
Aggregator
(Academic Institution )
Combination Analysis
Aggregated Hypothesis Performance Metrics
Hypothesis Performance Metrics
Analysis Definition Y
Analysis Definition Y
Analysis Definition Y
Hypothesis/Trial Methodology
How well did the trial method perform?
PCWG-Share-01: Data Flow

## Slide 7
PCWG-Share-01: Error Metric Definitions
See PCWG-Share-01 Definition Document for Further Details

## Slide 8
Time
June
Finalise Definition Doc
Finalise Analysis Tool
July
PCWG Participants work to set up their proprietary datasets
Aug
Roskilde
PCWG Meeting
Sep
US PCWG Meeting
Aggregate Initial results + Present
Oct
Aarhus
PCWG Meeting
Nov
EWEA Paris
Dec
London
PCWG Meeting
AWEA New Orleans
PCWG Participants perform further analysis
Aggregate final results + Present
Agree Conclusions
PCWG-Share-01: Timeline
Deadline for final results submission was 23rd November 2015.
Results were be combined by Data Aggregator (NREL) for presentation at the December 2015 PCWG meeting.

## Slide 9
PCWG-Share-01: PCWG Analysis Tool
Version | Comment | Submissions
0.5.8 (Beta 2) | Pre-release version used in a few of the RES submissions (identical to 0.5.8) | 52
0.5.8 | Version used in original round of submissions | 
0.5.9 | Changes to interpolation method (more later). No contribution to errors from unpopulated bins. | 47 (resubmissions)
0.5.10 | Slightly relaxed submission criteria (fewer populated bins required). | 

## Slide 10
PCWG-Share-01: Submission Map

## Slide 11
PCWG-Share-01: Submissions by Country

## Slide 12
PCWG-Share-01: Submissions by Participant Type

## Slide 13
PCWG-Share-01: Turbine Size vs Measurement Year

## Slide 14
Still unexpectedly large errors for baseline inner range
(further investigation required)
PCWG-Share-01: Baseline Error, Inner vs Outer Range
‘Uncertainty’ associated with
‘Outer Range’ effects.
Std Dev ≈ 2%
Smaller inner baseline errors still warrant further investigation
Version 0.5.9/10

## Slide 15
POWER CURVE
INTERPOLATION ISSUE

## Slide 16
What is inner range baseline error?
The Inner Range power curve is derived from the Inner Range data
Each Inner Range data point is compared to the Inner Range power curve. The error for each data point is calculated.
The error is summarised as NME (Normalised Mean Error). This is expected to be 0 for the inner range!
HOWEVER The inner range baseline error may not be 0 depending on interpolation of the power curve!
Inner Range Baseline Error
Error for each point is the difference from the interpolated power curve

## Slide 17
Zero-Order interpolation: easy to get 0 NME (just use the bin average power) but large errors for individual data points.

## Slide 18
Linear Interpolation: v0.5.8 and earlier, improvement for individual data points but noticeable over prediction at low wind speed

## Slide 19
Cubic interpolation: introduced in v0.5.9 for PCWG-Share-01. Noticeably reduces error at low wind speed compared to linear.

## Slide 20
Normalised Mean Error (NME) by wind speed:
Cubic interpolation has similar but smaller errors than linear.
Zero-order has 0 error by definition
Cubic and linear interpolators over estimate data at the ankle
Cubic and linear interpolators under estimate data at the knee

## Slide 21: Residual Error
Main reason for residual error: Bin averages are used as interpolation points. Unfortunately the bin averages do not lie exactly on the curve when the underlying function is non-linear.
Cubic
(Convex)
Clipped
(Concave)
Linear
The bin average, (avg(x), avg(y)),
is above the curve
The bin average, (avg(x), avg(y)),
is on the curve
The bin average, (avg(x), avg(y)),
is below the curve

## Slide 22: Possible solutions
The problem is that bin average power does not well represent bin centre power
The bin averaging process is very similar to the effect of turbulence. An iterative correction method similar to the Albers method could be applied to find the true bin centres.
In the rising part of the curve, evaluate bin average Cp, consider this to be bin centre Cp, and convert to bin centre power. Cp data is a bit less non-linear than power.

## Slide 23
PCWG-Share-01 RESULTS

## Slide 24
PCWG-Share-01: Baseline Errors by Wind Speed (0.5.8)
Large errors above rated for certain datasets.

## Slide 25
PCWG-Share-01: Baseline Errors by Wind Speed (0.5.9/10)

## Slide 26
PCWG-Share-01: PDM Errors by Wind Speed (0.5.9/10)

## Slide 27
PCWG-Share-01: Baseline Errors by Wind Speed (0.5.9/10)

## Slide 28
PCWG-Share-01: PDM Errors by Wind Speed (0.5.9/10)

## Slide 29
PCWG-Share-01: Baseline Errors by Wind Speed (0.5.9/10)

## Slide 30
PCWG-Share-01: Inner Baseline Errors by Wind Speed (0.5.9/10)

## Slide 31
PCWG-Share-01: Outer Baseline Errors by Wind Speed (0.5.9/10)

## Slide 32
PCWG-Share-01: Outer PDM Errors by Wind Speed (0.5.9/10)

## Slide 33
PCWG-Share-01: Outer Turbulence Errors by Wind Speed (0.5.9/10)

## Slide 34
PCWG-Share-01: REWS Errors by Wind Speed (0.5.9/10)

## Slide 35
PCWG-Share-01: REWS + Turb Errors by Wind Speed (0.5.9/10)

## Slide 36
PCWG-Share-01: Errors by Method (‘Four Cell Matrix’)

## Slide 37
PCWG-Share-01: Improvements by Method (‘Four Cell Matrix’)

## Slide 38
Many thanks to all PCWG-Share-01 Participants and special thanks to
Andy Clifton of NREL
Join the Power Curve Working Group at: www.pcwg.org