## Slide 1
PCWG
TI measurements offshore for power curve verification
and wind resource assessment
Colorado 6 October 2014
MOVING ENERGY FORWARD

## Slide 2: DONG Energy is one of the leading energy groups in Northern Europe
Our business is based on procuring, producing, distributing and trading in energy and related products in Northern Europe.
DONG Energy has 6,500 employees and is headquartered in Denmark.
Customers & Markets
Exploration & Production
Thermal Power
Wind Power

## Slide 3: Wind Power
Principal activity
Development, construction and operation of offshore wind farms
Market position
Market leader in offshore wind, has built 35% of European capacity
Strong pipeline of projects in lead-up to 2020
Strategic targets for 2020
Installed offshore wind capacity (gross installed): 6.5 GW
Reducing offshore wind Cost of Electricity to below EUR 100/MWh3
West Rijn
Breeveertien
Den Helder
Barrow
Burbo Bank
Gunfleet Sands 1+ 2
London Array 1
Walney 1+2
Nysted
Horns Rev 1
Lincs
Anholt
Borkum Riffgrund 1
WoDS
Walney Ext.
Burbo Bank Ext.
Hornsea Heron
Gode Wind 1+2
Outer Solway
Saint-Nazaire
Northern Ireland
Middelgrunden
Tunø knob
Vindeby
Hornsea Njord
Westermost Rough
Borkum Riffgrund 2
Borkum Riffgrund West 1
Courseulles-sur-Mer
Fécamp
Horns Rev 2
Avedøre Holme
Gode Wind 3+4
Race bank
Offshore projects in operation, under construction and development
Under construction
Under development
In operation

## Slide 4: TI measurements offshore for power curve verification
Relevance of TI measurements in the inner/outer range concept
Power curve verification offshore: two beam nacelle LIDAR
TI based on two beam nacelle LIDAR
Readiness from 3rd party independent testers in the use of nacelle LIDAR
Characterization of ambient offshore turbulence intensity in Northern Europe

## Slide 5: TI measurements in the inner/outer range concept
Inner Range: the range of conditions for which one can expect to achieve an Annual Energy Production (AEP) of 100% (relative to a reference power curve).
Outer Range: the range of conditions for which one can expect to achieve an AEP of less than 100%. Stated another way the outer range is the range of all possible conditions excluding those in the inner range. It is envisaged that suppliers may offer some level of reduced warranty for the outer range

## Slide 6: TI measurements in the inner/outer range concept
TI measurement as a good proxy for stability offshore
TI for offshore site classification (second part)
Focus on the inner range for power curve guarantees
Being able to measure "type B" performance issues (inner to WTG)
Eventual use other measurements to monitor atmospheric stability
(ground based /floating LIDARs / sea surface temperature)
Power curve test as a dialogue instrument for performance improvements
with WTG supplier

## Slide 7: Power curve verification offshore: two beam nacelle LIDAR
Nacelle-based LIDAR
IEC61400-12-1 Ed.1
Very costly offshore !
Cost effective solution

## Slide 8: Power curve verification offshore: two beam nacelle LIDAR
EUDP project lead by DTU: demonstration test at Avedøre

## Slide 9: Power curve verification offshore: two beam nacelle LIDAR
Comparison of results as outcome of the EUDP project lead by DTU
DTU Wind Energy E-0016

## Slide 10: Power curve verification offshore: two beam nacelle LIDAR
Comparison of results as outcome of the EUDP project lead by DTU
DTU Wind Energy E-0016

## Slide 11: TI based on two beam nacelle LIDAR
Comparison of results as outcome of the EUDP project lead by DTU
DTU Wind Energy E-0016
The lidar calibration uncertainty
2) The uncertainty due to the terrain orography
3) The uncertainty related to the measurement height (if this one goes out of the range hub height +/- 2.5%)
4) The uncertainty of the tilt inclinometers

## Slide 12: TI based on two beam nacelle LIDAR
Formulation use for computing TI with a two beam nacelle LIDAR
Arithmetic average of the TI of each beam :
DTU Wind Energy E-0016
Notes: Turbulence intensity on each beam is defined as the standard deviation dVi of each beam’s wind speed (i=0 or 1) divided by the average beam radial wind speed
the 10 minute average radial wind speeds are noted <V0> (for the left-hand line of sight when looking forward from behind the lidar optical head) and <V1> (for the right-hand line of sight).

## Slide 13: 3rd party independent testers readiness
Readiness1 is confirmed by:
5 different independent testers having participated in bids for testing services
3 different independent testers have been actively involved in the nacelle LIDAR power curve analysis
Lack of IEC standard does not compromise quality
Lack of IEC coverage may compromise acceptance from non technically well informed agents in our value change
1 EUDP program was published in January 2013

## Slide 14: TI measurements offshore for power curve verification
Relevance of TI measurements in the inner/outer range concept
Power curve verification offshore: two beam nacelle LIDAR
TI based on two beam nacelle LIDAR
Readiness from 3rd party independent testers in the use of nacelle LIDAR
Characterization of ambient offshore turbulence intensity in Northern Europe

## Slide 15: Characterization of Ambient Offshore Turbulence Intensity from Analysis of Nine Offshore Meteorological Masts in Northern Europe
Daniel Pollak
European Wind Energy Masters Program 2014
MSc Wind Energy Engineering –Tech. Univ. of Denmark 2014
MSc Engineering Wind Physics – Univ. of Oldenburg 2014
BSc Meteorology – Penn State 2011
NCAR/CU Intern Summers 2009-2012
Masters Thesis in collaboration with Nicolai Nygaard & Miriam Marchante Jiménez at DONG Energy and Rozenn Wagner and Ameya Sathe at DTU Risø Wind Energy.

## Slide 16
Motivation & Goals
Why TI is Important to Understand
Fatigue loads on turbine structure dependent on TI  knowledge of TI fosters optimal turbine design
To properly model wakes (lower turbulence results in slower wake recovery and more wake losses)  this work provides insight and could be used as input in future models
Of value to both research and industry
Turbulence Intensity (TI)
The degree of fluctuations about the mean wind speed within wind field
Data Availability
9 offshore met masts throughout Northern Europe
Scale hitherto not examined
Notes: Ambient Turbulence Intensity

## Slide 17
How do these turbulence parameters vary with wind speed (), height (z) and wind direction (θ) at the nine different sites?
Are these relationships regional or strictly site dependent?
How do the found trends compare with previous studies and the IEC 61400-3 standards for offshore wind turbine design?
How do these relationships vary with fetch or proximity to coast?
Thesis Research Questions
Turbulence Parameters
Discussed
σU – wind speed standard deviation
TI – ambient turbulence intensity
Notes: Could say why these four parameters are described.

## Slide 18
The Data – 9 Met Masts
Prevailing Westerlies
Prevailing Westerlies
A wealth of data with speed and direction data available at numerous heights
9 masts with 74 sets of wind speed data (1-3 obs per height)
Ranging from 7-111km from nearest land
10 minute data – analyzed in yearly periods to avoid intro of seasonal bias
Filtering criteria implemented; mast shadow corrected
1-5 years of data per mast between 2005-2013 (except M2)

## Slide 19
*IEC 61400-3 states that σU increases linearly with height.
*Not the case as slope changes around transition from thermal to wave-driven turbulence
σU vs Speed - Scatterplots
Thermal
Mechanical
*Bin where change occurs is height dependent (8-14 )
*Note persistence of low σUw at ↑U
*Lower heights see the influence of waves at lower wind speeds
Thermal
Mechanical
Notes: *Change more noticeable at F1

## Slide 20
TI vs Speed - Scatterplots
Thermal
Mechanical
F1
*IEC states that TI monotonically decreases, not the case offshore
*Change in slope of σU corresponds to minimum in TI curve due to transition between turbulence generating sources. (Height dependent : 8-14 m/s)
* More scatter with thermally driven turbulence: vast differences between TI observed in stable versus unstable conditions
*Decreasing TI with increasing z; further from air-sea interface

## Slide 21
Very similar trends, especially at 50, 70 and 80m. Less agreement at 30m
Same closeness observed with σU
Nearly universal relationship universal in Northern Europe when averaging over all wind directions, especially at high U
50m
All Mast Comparison – TI vs Speed
Wind Speed (m/s)
Turbulence Intensity

## Slide 22
* σU is unchanging with height
* σU increases linearly with height
* σσU invariant w/ height & U
* TI monotonically decreases w/ increasing wind speed
* TI unchanging with height
* Δσ equals equation above & unchanging with height
* σU, σσU increase w/ height @ ↑U
* σU experiences change in slope w/ increasing U (turb transition)
* σσU does vary some with U
* TI decreases until a height-dependent turbulence transition point after which TI increases
* Values for Δσ much larger and height-dependent
IEC 61400-3 Standard
Thesis Realizations
Standard is not sufficient for offshore applications. Wang (2013) suggested changes; This thesis could contribute to future analysis
IEC 61400-3 Standard: Discrepancies Found
Design Requirements for Offshore Wind Turbines
(Based on Onshore IEC 61400-1 Standard)

## Slide 23
σU Vertical Profile Dependence on Speed
Nearly constant with height at low speeds: thermal mixing
Strong decrease w/ height at high speeds due to generation of turbulence at air-sea interface
Slightly higher values at sites closer to land
Very similar trend seen in TI

## Slide 24
Regional Similarities – Vertical Wind Profile
One of key differentiable features between masts is proximity to shore
Similarities in average wind speed and average TI seen between masts within similar geographic region
Four regions demarked for the directional dependency analysis
Far Offshore Region – HO, F1, F3
East Coast UK – HU, LA
West UK / Irish Sea – SF1, SF2
West Coast DK – F3, M2, M8
Utilized Google Earth Measurement Tools
Notes: Important to note that some differences could be due to inter-annual variability in general atmos flow.
HO’s slower profile likely due to data gap in winter months, when wind speeds are generally the largest.
The directional dependencies on TI were found here to be highly depedent on region, but rather similar within the regions. This is due to the influences of the local mesoscale meteorologcial conditions and geographical details. To show the differences between regions and similarities within regions, plots of TI vs theta are generated for each mast.
MAKE SURE CLEARLY EXPLAIN ALL OF THE FOLLOWING PLOTS WELL!!
Mention Google Earth’s use

## Slide 25
TI decreases with increasing fetch up until 40-50 km from coast  due to lower roughness offshore
Thereafter, TI increases slightly with increasing fetch  fully developed waves and larger swell
TI Not Necessarily Monotonic with Fetch
TI @ Height Closest to 50m
At all sites with swaths of fetch >100-200 km, the largest TI values were observed in these sectors. For sites when the nearest land < 40 km, additional factors contribute to max TI sectors.

## Slide 26
Far Offshore is >40 km from coast
TI larger in sectors with fetch >200 km and lowest in land sectors
Also observed in other regions
F1
TI vs θ – Far Offshore Region (F1, F3, HO)

## Slide 27
Conclusions
σU, TI examined for dependencies on U, z, θ
Average TI at 50m ranged from 6.3 to 7.4%
σU increases with speed as expected, but not linearly as in IEC and after the turbulence transition, TI begins to increase with increasing wind speed, also contrary to the IEC standard
σU ,TI vs. U – strong similarity in trends indicating a nearly universal relationship across Northern Europe, especially at higher heights
Fetch found to be vital proxy for directional dependence on TI. TI decreases with increasing fetch until ~50km where it increased
TI predominantly is maximized in sectors with fetch >100-200 km (well-developed waves and swell)
At sites closer to shore, factors such as mountains and coastal orientation also lead to max TI sectors.
σU , TI profiles (w/ height) show strong dependence on wind regime. At low speeds uniform with height, thermally driven turbulence; at high speeds, rapid decrease with z as distance from sea surface decreases