## Slide 1: Inflow angle and Energy Production
Jørgen Højstrup
Wind Solutions / Højstrup Wind Energy
Power Curve Working Group, Louisville
6 October 2014

## Slide 2: CONTENTS
  Energy loss by non-zero inflow angle
  Directional variation
  Inflow angles and energy loss from real sites

## Slide 3: Factors influencing Power Curve
  Wind speed
  Air density
  Turbulence intensity
  Directional variation
  Inflow angle
  Wind shear
  Vertical wind veer

## Slide 4: Inflow angle negligible?
  Wind speed
  Air density
  Turbulence intensity
  Directional variation
  Inflow angle
  Wind shear
  Vertical wind veer

## Slide 5: Inflow angle negligible?
  - For conventional IEC 61400-12-1 verification
  Expensive and difficult to erect masts in sloping terrain
  High uncertainty on site calibration
  Most often you select turbines for PC verification in more benign terrain with small inflow angles
  With Spinner Anemometer and LIDAR verification there are no practical problems in doing PC verification also in complex terrain.

## Slide 6
Calculate Energy Loss
Wind vector
Component that generates energy
Yaw error
15 deg yaw error
AEP lost:

## Slide 7: Yaw- (and inflow-) error => Lower Production

## Slide 8: The “Usual” turbulence effect on power curve, but there is more ...

## Slide 9: Energy loss by directional variations

## Slide 10: Energy loss by directional variations

## Slide 11: Average inflow angle (calculated) 15 recent sites, 270 turbines

## Slide 12: Rotor not tilted: avg 0.5% energy lost

## Slide 13: Rotor tilt 4 deg: avg 1.8% energy loss

## Slide 14: Rotor tilt 6 deg: avg 2.8% energy loss

## Slide 15: CONCLUSIONS
Inflow angle can have significant influence on energy production
  Range 0 – 8 %
  Average 2.8 % for 6 deg rotor tilt

## Slide 16: Thank you for your attention
Højstrup Wind Energy & Wind Solutions
www.wind-solutions.com
Jorgen@hojstrup.eu