## Slide 1: Power curve loss adjustments at AWS Truepower: a 2016 update
Dan Bernadett
Chief Engineer

## Slide 2: Background
As part of the May 2012 study comparing actual to predicted performance, AWST identified power curves as the primary reason that actual performance fell below predicted levels.
Since this time, AWST has performed power curve tests ourselves and worked with a number of manufacturers and clients to gather measured power curve data in order to make site-specific power curve loss adjustments.

## Slide 3: Overview of Key Findings
Performance measurements of commercial units did not validate prototype results
Variability of power curve tests means that a larger sample is required to eliminate oscillation of loss estimate

## Slide 4: Power Curve Loss Adjustment Procedure
Losses are calculated by comparing the advertised and measured power curves
AEP is calculated for each curve using the wind speed frequency distribution for the site under consideration
A percent loss is determined by comparing the AEP using the advertised versus measured power curves

## Slide 5: Power Curve Loss Adjustment Procedure (details)
Power curve must be IEC-compliant and performed on the turbine model under consideration by a 3rd party at conditions representing those of the site.
Turbine models are defined by the rotor diameter and rated power
Changes to rotor diameter or rated power define a new turbine model and typically revert to the default power curve loss
Peak Cp values within the tests conducted by AWST fall in the range of 0.44 to 0.51. If measured results are received with peak Cp outside this range, AWST will consider excluding these values from the database.
Notes: Introduction
As part of the May 2012 study comparing actual to predicted performance, AWS Truepower (AWST) identified power curves as the primary reason that actual performance fell below predicted levels. Since this time, AWST has worked with a number of manufacturers and clients to gather measured power curve data in order to make site-specific power curve loss adjustments. This document describes the procedure for determination of the site specific loss.
Contract Language
AWST has assembled a document describing each loss and what data is required to adjust it to match conditions specific to the site. One of the ways in which losses can be adjusted is by providing AWST with the ability to review the contract language regarding the power curve warranty. Typically, the warranty language specifies that liquidated damages will apply if the measured results are a certain percentage (often 3-5%) below the advertised level. If the warranty calls for liquidated damages when this gap is smaller than the 2.4% default power curve level without exceptions for uncertainty or data filtering, the power curve loss will be reduced to reflect the contract language.
Power Curve Measurements
The power curve loss can also be adjusted based on tabular measurement results from an IEC-compliant test performed on the turbine model under consideration by a 3rd party at conditions representing those of the site. Note that tests conducted on prototype turbines cannot be used to make power curve loss adjustments. Prototype turbines are generally the only turbine model of that type at a site. Also, peak Cp values within the tests conducted by AWST fall in the range of 0.44 to 0.51. If measured results are received with peak Cp outside this range, AWST will consider excluding these values from the database.
Using a hub height frequency distribution representative of the project site, the annual energy production (AEP) will be calculated using the selected measured power curves and compared to the AEP using the advertised curve. The results of this assessment can be used in a “Direct” or “Hybrid” loss adjustment.
Power curve losses are applied using the following criteria:
Direct loss
The direct loss is applied when we have at least six power curves from the turbine model under consideration in conditions (shear and TI) that represent the site for at least three separate commercial wind farms. Turbulence Intensity (TI) and shear conditions for a test are considered representative of a project if the averages are within 5% and 0.1 respectively. The direct loss is calculated as the average result of the power curve tests for the turbine model under consideration.
Hybrid loss
The hybrid loss is an average of the 2.4% default loss and the direct loss. The hybrid loss is applied in the following situations:
  The loss is applied when we have at least four power curves from the turbine model under consideration in conditions (shear and TI) that represent the site for at least two separate commercial wind farms. The loss is calculated as the average of the default loss with the average of the results of the power curve tests for the turbine model under consideration.
Standard Loss (2.4%)
The standard loss (2.4%) is applied when we have insufficient information for the turbine model under consideration.
It should be noted, we do not assume performance exceeds the advertised value at the project under consideration even if tests at other sites show performance above advertised values. This is because the site under consideration may have turbulence, shear, or other conditions that cause performance to be worse than tests at other sites. Over-performance of test turbines will be noted in the report, but credit will not be given in the report for over-performance of tests at other sites. However, if the results provided ARE from the project site and turbine model under consideration, we would use the calculated loss value.
If the power curve loss using the above process shows a higher loss than the 2.4% default, the calculated power curve loss will be used. The default loss value of 2.4% was the average of historical power curve tests results, so it is expected that occasionally power curve results will come in below this value.
2012 Backcast Study: A Review and Calibration of AWS Truepower’s Energy Estimation Methods, AWS Truepower May 2012, Bernadett et. al.
AWS Truepower Loss and Uncertainty Memorandum 22 Jun 2016.pdf

## Slide 6: Power Curve Loss Adjustment Procedure (details cont.)
Using a hub height frequency distribution representative of the project site, the annual energy production (AEP) will be calculated using the selected measured power curves and compared to the AEP using the advertised curve. The results of this assessment can be used in a “Direct” or “Hybrid” loss adjustment. Power curve losses are applied using the following criteria:
Direct loss
The direct loss is applied when we have at least six power curves from the turbine model under consideration in conditions (shear and TI) that represent the site for at least three separate commercial wind farms. Turbulence Intensity (TI) and shear conditions for a test are considered representative of a project if the averages are within 5% and 0.1 respectively. The direct loss is calculated as the average result of the power curve tests for the turbine model under consideration.
Hybrid loss
The hybrid loss is an average of the 2.4% default loss and the direct loss. The hybrid loss is applied in the following situations:
  The loss is applied when we have at least four power curves from the turbine model under consideration in conditions (shear and TI) that represent the site for at least two separate commercial wind farms. The loss is calculated as the average of the default loss with the average of the results of the power curve tests for the turbine model under consideration.
Notes: Introduction
As part of the May 2012 study comparing actual to predicted performance, AWS Truepower (AWST) identified power curves as the primary reason that actual performance fell below predicted levels. Since this time, AWST has worked with a number of manufacturers and clients to gather measured power curve data in order to make site-specific power curve loss adjustments. This document describes the procedure for determination of the site specific loss.
Contract Language
AWST has assembled a document describing each loss and what data is required to adjust it to match conditions specific to the site. One of the ways in which losses can be adjusted is by providing AWST with the ability to review the contract language regarding the power curve warranty. Typically, the warranty language specifies that liquidated damages will apply if the measured results are a certain percentage (often 3-5%) below the advertised level. If the warranty calls for liquidated damages when this gap is smaller than the 2.4% default power curve level without exceptions for uncertainty or data filtering, the power curve loss will be reduced to reflect the contract language.
Power Curve Measurements
The power curve loss can also be adjusted based on tabular measurement results from an IEC-compliant test performed on the turbine model under consideration by a 3rd party at conditions representing those of the site. Note that tests conducted on prototype turbines cannot be used to make power curve loss adjustments. Prototype turbines are generally the only turbine model of that type at a site. Also, peak Cp values within the tests conducted by AWST fall in the range of 0.44 to 0.51. If measured results are received with peak Cp outside this range, AWST will consider excluding these values from the database.
Using a hub height frequency distribution representative of the project site, the annual energy production (AEP) will be calculated using the selected measured power curves and compared to the AEP using the advertised curve. The results of this assessment can be used in a “Direct” or “Hybrid” loss adjustment.
Power curve losses are applied using the following criteria:
Direct loss
The direct loss is applied when we have at least six power curves from the turbine model under consideration in conditions (shear and TI) that represent the site for at least three separate commercial wind farms. Turbulence Intensity (TI) and shear conditions for a test are considered representative of a project if the averages are within 5% and 0.1 respectively. The direct loss is calculated as the average result of the power curve tests for the turbine model under consideration.
Hybrid loss
The hybrid loss is an average of the 2.4% default loss and the direct loss. The hybrid loss is applied in the following situations:
  The loss is applied when we have at least four power curves from the turbine model under consideration in conditions (shear and TI) that represent the site for at least two separate commercial wind farms. The loss is calculated as the average of the default loss with the average of the results of the power curve tests for the turbine model under consideration.
Standard Loss (2.4%)
The standard loss (2.4%) is applied when we have insufficient information for the turbine model under consideration.
It should be noted, we do not assume performance exceeds the advertised value at the project under consideration even if tests at other sites show performance above advertised values. This is because the site under consideration may have turbulence, shear, or other conditions that cause performance to be worse than tests at other sites. Over-performance of test turbines will be noted in the report, but credit will not be given in the report for over-performance of tests at other sites. However, if the results provided ARE from the project site and turbine model under consideration, we would use the calculated loss value.
If the power curve loss using the above process shows a higher loss than the 2.4% default, the calculated power curve loss will be used. The default loss value of 2.4% was the average of historical power curve tests results, so it is expected that occasionally power curve results will come in below this value.
2012 Backcast Study: A Review and Calibration of AWS Truepower’s Energy Estimation Methods, AWS Truepower May 2012, Bernadett et. al.
AWS Truepower Loss and Uncertainty Memorandum 22 Jun 2016.pdf

## Slide 7: Power Curve Loss Adjustment Procedure (more details)
Standard Loss (2.4%)
The standard loss (2.4%) is applied when we have insufficient information for the turbine model under consideration.
We do not assume performance exceeds the advertised value at the project under consideration even if tests at other sites show performance above advertised values. This is because the site under consideration may have turbulence, shear, or other conditions that cause performance to be worse than tests at other sites. Over-performance of test turbines will be noted in the report, but credit will not be given in the report for over-performance of tests at other sites. However, if the results provided ARE from the project site and turbine model under consideration, we would use the calculated loss value.
If the power curve loss using the above process shows a higher loss than the 2.4% default, the calculated power curve loss will be used. The default loss value of 2.4% was the average of historical power curve tests results, so it is expected that occasionally power curve results will have higher losses
Notes: Introduction
As part of the May 2012 study comparing actual to predicted performance, AWS Truepower (AWST) identified power curves as the primary reason that actual performance fell below predicted levels. Since this time, AWST has worked with a number of manufacturers and clients to gather measured power curve data in order to make site-specific power curve loss adjustments. This document describes the procedure for determination of the site specific loss.
Contract Language
AWST has assembled a document describing each loss and what data is required to adjust it to match conditions specific to the site. One of the ways in which losses can be adjusted is by providing AWST with the ability to review the contract language regarding the power curve warranty. Typically, the warranty language specifies that liquidated damages will apply if the measured results are a certain percentage (often 3-5%) below the advertised level. If the warranty calls for liquidated damages when this gap is smaller than the 2.4% default power curve level without exceptions for uncertainty or data filtering, the power curve loss will be reduced to reflect the contract language.
Power Curve Measurements
The power curve loss can also be adjusted based on tabular measurement results from an IEC-compliant test performed on the turbine model under consideration by a 3rd party at conditions representing those of the site. Note that tests conducted on prototype turbines cannot be used to make power curve loss adjustments. Prototype turbines are generally the only turbine model of that type at a site. Also, peak Cp values within the tests conducted by AWST fall in the range of 0.44 to 0.51. If measured results are received with peak Cp outside this range, AWST will consider excluding these values from the database.
Using a hub height frequency distribution representative of the project site, the annual energy production (AEP) will be calculated using the selected measured power curves and compared to the AEP using the advertised curve. The results of this assessment can be used in a “Direct” or “Hybrid” loss adjustment.
Power curve losses are applied using the following criteria:
Direct loss
The direct loss is applied when we have at least six power curves from the turbine model under consideration in conditions (shear and TI) that represent the site for at least three separate commercial wind farms. Turbulence Intensity (TI) and shear conditions for a test are considered representative of a project if the averages are within 5% and 0.1 respectively. The direct loss is calculated as the average result of the power curve tests for the turbine model under consideration.
Hybrid loss
The hybrid loss is an average of the 2.4% default loss and the direct loss. The hybrid loss is applied in the following situations:
  The loss is applied when we have at least four power curves from the turbine model under consideration in conditions (shear and TI) that represent the site for at least two separate commercial wind farms. The loss is calculated as the average of the default loss with the average of the results of the power curve tests for the turbine model under consideration.
Standard Loss (2.4%)
The standard loss (2.4%) is applied when we have insufficient information for the turbine model under consideration.
It should be noted, we do not assume performance exceeds the advertised value at the project under consideration even if tests at other sites show performance above advertised values. This is because the site under consideration may have turbulence, shear, or other conditions that cause performance to be worse than tests at other sites. Over-performance of test turbines will be noted in the report, but credit will not be given in the report for over-performance of tests at other sites. However, if the results provided ARE from the project site and turbine model under consideration, we would use the calculated loss value.
If the power curve loss using the above process shows a higher loss than the 2.4% default, the calculated power curve loss will be used. The default loss value of 2.4% was the average of historical power curve tests results, so it is expected that occasionally power curve results will come in below this value.
2012 Backcast Study: A Review and Calibration of AWS Truepower’s Energy Estimation Methods, AWS Truepower May 2012, Bernadett et. al.
AWS Truepower Loss and Uncertainty Memorandum 22 Jun 2016.pdf

## Slide 8: Requirements for Power Curve Loss Adjustment
Plants required for direct loss | 3
Turbines required for direct loss | 6
Plants required for hybrid loss | 2
Turbines required for hybrid loss | 4
Credit for one plant? | No
Prototypes included? | No

## Slide 9: Contract Language
Typically, the warranty language specifies that liquidated damages will apply if the measured results are a certain percentage (often 3-5%) below the advertised level.
If the warranty calls for liquidated damages when this gap is smaller than the 2.4% default power curve level without exceptions for uncertainty or data filtering, the power curve loss will be reduced to reflect the contract language.
Notes: Introduction
As part of the May 2012 study comparing actual to predicted performance, AWS Truepower (AWST) identified power curves as the primary reason that actual performance fell below predicted levels. Since this time, AWST has worked with a number of manufacturers and clients to gather measured power curve data in order to make site-specific power curve loss adjustments. This document describes the procedure for determination of the site specific loss.
Contract Language
AWST has assembled a document describing each loss and what data is required to adjust it to match conditions specific to the site. One of the ways in which losses can be adjusted is by providing AWST with the ability to review the contract language regarding the power curve warranty. Typically, the warranty language specifies that liquidated damages will apply if the measured results are a certain percentage (often 3-5%) below the advertised level. If the warranty calls for liquidated damages when this gap is smaller than the 2.4% default power curve level without exceptions for uncertainty or data filtering, the power curve loss will be reduced to reflect the contract language.
Power Curve Measurements
The power curve loss can also be adjusted based on tabular measurement results from an IEC-compliant test performed on the turbine model under consideration by a 3rd party at conditions representing those of the site. Note that tests conducted on prototype turbines cannot be used to make power curve loss adjustments. Prototype turbines are generally the only turbine model of that type at a site. Also, peak Cp values within the tests conducted by AWST fall in the range of 0.44 to 0.51. If measured results are received with peak Cp outside this range, AWST will consider excluding these values from the database.
Using a hub height frequency distribution representative of the project site, the annual energy production (AEP) will be calculated using the selected measured power curves and compared to the AEP using the advertised curve. The results of this assessment can be used in a “Direct” or “Hybrid” loss adjustment.
Power curve losses are applied using the following criteria:
Direct loss
The direct loss is applied when we have at least six power curves from the turbine model under consideration in conditions (shear and TI) that represent the site for at least three separate commercial wind farms. Turbulence Intensity (TI) and shear conditions for a test are considered representative of a project if the averages are within 5% and 0.1 respectively. The direct loss is calculated as the average result of the power curve tests for the turbine model under consideration.
Hybrid loss
The hybrid loss is an average of the 2.4% default loss and the direct loss. The hybrid loss is applied in the following situations:
  The loss is applied when we have at least four power curves from the turbine model under consideration in conditions (shear and TI) that represent the site for at least two separate commercial wind farms. The loss is calculated as the average of the default loss with the average of the results of the power curve tests for the turbine model under consideration.
Standard Loss (2.4%)
The standard loss (2.4%) is applied when we have insufficient information for the turbine model under consideration.
It should be noted, we do not assume performance exceeds the advertised value at the project under consideration even if tests at other sites show performance above advertised values. This is because the site under consideration may have turbulence, shear, or other conditions that cause performance to be worse than tests at other sites. Over-performance of test turbines will be noted in the report, but credit will not be given in the report for over-performance of tests at other sites. However, if the results provided ARE from the project site and turbine model under consideration, we would use the calculated loss value.
If the power curve loss using the above process shows a higher loss than the 2.4% default, the calculated power curve loss will be used. The default loss value of 2.4% was the average of historical power curve tests results, so it is expected that occasionally power curve results will come in below this value.
2012 Backcast Study: A Review and Calibration of AWS Truepower’s Energy Estimation Methods, AWS Truepower May 2012, Bernadett et. al.
AWS Truepower Loss and Uncertainty Memorandum 22 Jun 2016.pdf

## Slide 10: Effect of Power Curve Loss
Under current procedure, 12% of projects since Jun 2015 would have been adjusted, and the average adjustment would have been 0.2%.
Average impact on all projects using current procedure is 0.024%

## Slide 11: Prototypes
Power performance levels of prototype turbines can be different from production turbines
The best commercial turbines match prototype results
Prototypes do not represent the poor performance seen on some commercial turbines
Commercial performance on average 0.6% below prototype
AWS Truepower will eliminate prototypes from consideration for loss adjustments
Prototypes are defined as turbines that are unique at that site

## Slide 12: Distribution of prototype versus commercial tests
Chart: A=9, k=2.5
| 0.85 | 0.86 | 0.87 | 0.88 | 0.89 | 0.9 | 0.91 | 0.92 | 0.93 | 0.94 | 0.95 | 0.96 | 0.97 | 0.98 | 0.99 | 1 | 1.01 | 1.02 | 1.03 | 1.04 | 1.05 | 1.06 | 1.07 | 1.08 | 1.0900000000000001 | 1.1000000000000001 | 1.1100000000000001 | 1.1200000000000001 | 1.1299999999999999 | 1.1399999999999999 | 1.1499999999999999
Commercial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 3 | 11 | 20 | 24 | 19 | 11 | 4 | 2 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Prototype | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 4 | 6 | 13 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fitted | 9.8162e-08 | 1.2715e-06 | 1.368e-05 | 0.00012225 | 0.0009075 | 0.0055957 | 0.02866 | 0.12193 | 0.43087 | 1.2647 | 3.0837 | 6.2452 | 10.5059 | 14.6804 | 17.0393 | 16.4278 | 13.1558 | 8.7512 | 4.8354 | 2.2193 | 0.84605 | 0.26791 | 0.07047 | 0.015397 | 0.0027943 | 0.00042123 | 5.2744e-05 | 5.4859e-06 | 4.7395e-07 | 3.4012e-08 | 2.0274e-09
Fitted_prototype | 1.0427e-21 | 8.1505e-19 | 4.0215e-16 | 1.2525e-13 | 2.4622e-11 | 3.0554e-09 | 2.3932e-07 | 1.1833e-05 | 0.00036928 | 0.0072746 | 0.090457 | 0.70999 | 3.5176 | 11.0006 | 21.7152 | 27.0577 | 21.2812 | 10.5653 | 3.3109 | 0.65492 | 0.081773 | 0.0064448 | 0.00032062 | 1.0068e-05 | 1.9957e-07 | 2.4969e-09 | 1.972e-11 | 9.8304e-14 | 3.0933e-16 | 6.144e-19 | 7.7031e-22

## Slide 13: Effect of Inclusion of New Power Curve Data
We encourage our clients to provide data
However, we want our loss estimate to change smoothly when new data is included.
Example of data inclusion under old rules
Example of data inclusion under new rules
Chart: 
 | -0.012615 | -0.00076074 | -0.0072119 | -0.005238 | -0.001669 | -0.001659
Chart: 
 | -0.024 | -0.01238 | -0.0072119 | -0.005238 | -0.001669 | -0.001659

## Slide 14: Going Forward
Loss adjustments going forward will be limited to cases where AWST is able to validate effect on production