## Slide 1: OEM specific power curve losses – a practical case
PCWG – Copenhagen

## Slide 2: Motivation: Incorporate OEM data to develop vendor specific view on turbine performance.
Challenges
Need to preserve confidentiality of test data
Analysis must stand test of internal and external scrutiny
How to use historic data to predict future performance

## Slide 3: Overview
Methodology
Analysis
Conclusions
What’s next.

## Slide 4: Methodology

## Slide 5: Methodology
Use shareable PPT data to agree on analysis technique
Using version of PCWG ShareX tool to produce turbine performance matrixes.
Combining individual test matrixes to produce platform specific matrix
2 core matrixes produced: one showing power deviation to average measured power curve, one showing power deviation to warranted power curve.
DNV GL to review provided matrixes and compare the following:
OEM matrix relative to average to DNV GL matrix relative to average
With and without matched data coverage
OEM matrix relative to average to OEM matrix relative to guaranty
DNG GL matrix + “bulk” to OEM matrix relative to guaranty
Extrapolation to future curves by “Power Curve Benchmarking”

## Slide 6: Analysis

## Slide 7: Data provided
Turbine type | Number of tests
Type A | ~15
Type B | >20
Type C | 2
Type D | ~10

## Slide 8: Overall results – rounded to 0.5%
 | OEM average compared to DNV GL average - not matched | OEM average compared to DNV GL average - matched | OEM warranted compared to DNV GL average - matched
Type A | 99.5% | 99.5% | 98.0%
Type B | 100.0% | 100.0% | 99.5%
Type C | 99.0% | 99.0% | 101.0%
Type D-1 | 99.5% | 99.5% | 99.5%
Type D-2 | 99.5% | 99.5% | 99.5%
Comparing these columns indicates the impact of data coverage on the results
Comparing these columns indicates the difference between the average and the guaranty
Only two tests!

## Slide 9: Power curve benchmark – guaranteed curves

## Slide 10: Concerns/Outstanding issues
Seasonality of tests
Treatment of rated power
Completing 3rd party traceability

## Slide 11: Conclusions

## Slide 12: Conclusions
Method successfully allowed individual parties concerns to be addressed while still providing independently auditable conclusions to be developed
Reduction in turbine performance loss and uncertainty achieved on a commercial project.
Performance of Type B well understood
Number of tests needed to reach stable matrix seems to be >10
Need to be able to extrapolate to new technology
  Power Curve benchmarking seems a reasonable approach while waiting for measured curves to be provided.

## Slide 13: What’s next.

## Slide 14: What’s next?
Better understanding of new technology
  New data from Type D platform becoming available, as well as other larger rotor platforms
  Further validation of the Power Curve Benchmarking method

## Slide 15: Questions?
Taylor Geer
taylor.geer@dnvgl.com
@taylorgeer1