## Slide 1: New Approaches to Power Curve Adjustments in WakeBlaster
(c) ProPlanEn, 2018
Philip Bradstock
Power Curve Working Group
1 February 2018, Hamburg

## Slide 2: WakeBlaster
Measurements (SCADA or virtual)
3D RANS Wake Model
Power Capture

## Slide 3: Power Capture Corrections
Turbulence
Air Density
Rotor Equivalent Wind Speed (REWS)
  Shear
  Wake profile
Yaw Misalignment

## Slide 4: Turbulence – Zero Turbulence Power Curve
Current IEC method assumes constant Cp below rated:
  Not true at low wind-speeds.
  Not true just below rated
Chart: Wind Speed (m/s)
| 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 11.4 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Cp (NREL) | 0.19641 | 0.36356 | 0.42308 | 0.44713 | 0.4532 | 0.45294 | 0.45237 | 0.45152 | 0.44884 | 0.44189 | 0.37887 | 0.29799 | 0.23859 | 0.19398 | 0.15984 | 0.13326 | 0.11226 | 0.095449 | 0.081836 | 0.070693 | 0.061484 | 0.053808 | 0.047359 | 0.0419
Cp (IEC) | 0.4532 | 0.4532 | 0.4532 | 0.4532 | 0.4532 | 0.4532 | 0.4532 | 0.4532 | 0.4532 | 0.44189 | 0.37887 | 0.29799 | 0.23859 | 0.19398 | 0.15984 | 0.13326 | 0.11226 | 0.095449 | 0.081836 | 0.070693 | 0.061484 | 0.053808 | 0.047359 | 0.0419
Power (NREL) | 40.5 | 177.7 | 403.9 | 737.6 | 1187.2 | 1771.1 | 2518.6 | 3448.4 | 4562.5 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
Power (IEC) | 93.4531 | 221.5184 | 432.6531 | 747.6245 | 1187.2 | 1772.1469 | 2523.2327 | 3461.2245 | 4606.8898 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000

## Slide 5: Zero TI power curve - Alternative Method
Taylor Series Expansion of TI=0 power curve about mean wind speed (assume cubic relationship).
10-minute mean by Gaussian Integration:
=> expression relating zero turbulence and 10-minute mean power curves.
= power = wind speed = 10-min mean wind speed = turbulence intensity

## Slide 6: Zero TI power curve - Alternative Method
Apex Correction:
Warning: Iteration has a tendency to diverge – limit number of iterations
Find point of inflection and extrapolate with cubic
Rated Power Correction:
Limit all values to rated power
Finite difference method:
Chart: 
Chart: 

## Slide 7: Alternative Method Testing
Measured 10-min power curve
TI=0 power curve
Simulated 10-min power curve
Chart: 
| 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
IEC | 33.3502 | 28.5066 | 26.0873 | 22.4369 | 13.9829 | -6.8956 | -8.9944 | -10.3642 | 3.6332 | -3.0891 | -1.7767 | -2.7144
WakeBlaster | -1.9104 | -0.4543 | 0.1314 | -1.4109 | 4.58 | 2.7342 | 7.5453 | 2.0713 | 10.152 | -0.2791 | -0.6881 | -2.3189
Chart: 
| 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
IEC | 25.9687 | 26.5531 | 11.1358 | 5.1563 | 7.5275 | -3.9601 | -38.7104 | -54.2785 | -20.7813 | -5.2444 | -0.9854 | -0.2204 | -0.084
WakeBlaster | 1.4394 | -0.2997 | 0.5453 | -2.6925 | -3.1821 | 6.3471 | -9.4728 | -36.0787 | -14.8329 | -3.8146 | -0.6554 | -0.1131 | -0.0189

## Slide 8: Alternative Method Testing
Measured 10-min power curve
TI=0 power curve
Simulated 10-min power curve
Chart: 
| 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
IEC | 46.5363 | 37.9606 | 27.2585 | 16.6941 | 3.4519 | -11.1649 | 14.0773 | 25.4613 | -7.7769 | -9.2485 | -1.9879 | -0.4632
WakeBlaster | -1.4062 | -0.5183 | 0.0478 | 0.1978 | -2.7425 | -4.1684 | 23.9494 | 30.4338 | -6.1757 | -8.8001 | -1.8327 | -0.3733
Chart: 
| 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
IEC | 62.8192 | 96.5768 | 76.6977 | 48.4695 | 16.9653 | -0.0002 | 19.5863 | 206.8379 | 255.3632 | -6.9319 | -12.1486 | -1.3735 | -0.3248
WakeBlaster | -16.8392 | 0.0021 | -0.0151 | 0.015 | 0.0427 | -0.1195 | 1.8988 | -4.4687 | 36.4465 | 4.4085 | -0.2572 | -0.0018 | 0

## Slide 9: Air Density Adjustment
IEC method:
Svenningsen method (semi-empirical):
“because varies with ”
= reference air density (1.225)
= alternate air density
= wind speed dependent exponent

## Slide 10: Air Density Adjustment
directly,
Chart: Cp-TSR curve
| 2.0169307999999999 | 2.2413694999999998 | 2.465808 | 2.7350501999999999 | 3.0939000000000001 | 3.2956150000000002 | 3.4523861 | 3.6091852000000002 | 3.7659563999999999 | 3.9003117 | 4.0346390000000003 | 4.1463823 | 4.2806259999999998 | 4.4373129999999996 | 4.5940285000000003 | 4.7508553999999998 | 4.9525703999999999 | 5.1991449999999997 | 5.4681635000000002 | 5.8269013999999997 | 6.1183075999999996 | 6.4996289999999997 | 6.9035343999999998 | 7.3074960000000004 | 7.6665979999999996 | 7.9583680000000001 | 8.2726100000000002 | 8.6318239999999999 | 9.0134530000000002 | 9.4175825 | 9.7767959999999992 | 10.158537000000001 | 10.472891000000001 | 10.832160999999999 | 11.213958 | 11.708059 | 12.112299999999999 | 12.494182 | 12.83112 | 13.235473000000001 | 13.594938000000001 | 13.931903999999999 | 14.246510000000001 | 14.561031 | 14.830721 | 15.122799000000001 | 15.414961 | 15.662179 | 15.954370000000001 | 16.313807000000001 | 16.628412000000001 | 16.987879 | 17.324928
Cp | 0.0038738 | 0.0038994 | 0.003925 | 0.010106 | 0.028598 | 0.049122 | 0.073741 | 0.09631 | 0.12093 | 0.1435 | 0.16811 | 0.20298 | 0.23374 | 0.26451 | 0.29323 | 0.31375 | 0.33428 | 0.35686 | 0.37944 | 0.40613 | 0.43281 | 0.44926 | 0.45545 | 0.45755 | 0.45753 | 0.45753 | 0.45561 | 0.44745 | 0.44134 | 0.43114 | 0.42298 | 0.40867 | 0.39846 | 0.3862 | 0.36779 | 0.34325 | 0.32484 | 0.30028 | 0.27982 | 0.25322 | 0.2266 | 0.20409 | 0.17543 | 0.15291 | 0.12629 | 0.10377 | 0.075104 | 0.05053 | 0.019812 | -0.0047484 | -0.033414 | -0.060025 | -0.088688
curve is designed to be quite flat at the peak.
Optimal TSR in centre of flat region.
Controller keeps turbine at optimal TSR by managing torque-speed relationship
= tip-speed ratio

## Slide 11: Air Density Adjustment
directly,
curve is designed to be quite flat at the peak.
Optimal TSR in centre of flat region.
Controller keeps turbine at optimal TSR by managing torque-speed relationship
Chart: Cp-TSR curve
| 2.0169307999999999 | 2.2413694999999998 | 2.465808 | 2.7350501999999999 | 3.0939000000000001 | 3.2956150000000002 | 3.4523861 | 3.6091852000000002 | 3.7659563999999999 | 3.9003117 | 4.0346390000000003 | 4.1463823 | 4.2806259999999998 | 4.4373129999999996 | 4.5940285000000003 | 4.7508553999999998 | 4.9525703999999999 | 5.1991449999999997 | 5.4681635000000002 | 5.8269013999999997 | 6.1183075999999996 | 6.4996289999999997 | 6.9035343999999998 | 7.3074960000000004 | 7.6665979999999996 | 7.9583680000000001 | 8.2726100000000002 | 8.6318239999999999 | 9.0134530000000002 | 9.4175825 | 9.7767959999999992 | 10.158537000000001 | 10.472891000000001 | 10.832160999999999 | 11.213958 | 11.708059 | 12.112299999999999 | 12.494182 | 12.83112 | 13.235473000000001 | 13.594938000000001 | 13.931903999999999 | 14.246510000000001 | 14.561031 | 14.830721 | 15.122799000000001 | 15.414961 | 15.662179 | 15.954370000000001 | 16.313807000000001 | 16.628412000000001 | 16.987879 | 17.324928
Cp | 0.0038738 | 0.0038994 | 0.003925 | 0.010106 | 0.028598 | 0.049122 | 0.073741 | 0.09631 | 0.12093 | 0.1435 | 0.16811 | 0.20298 | 0.23374 | 0.26451 | 0.29323 | 0.31375 | 0.33428 | 0.35686 | 0.37944 | 0.40613 | 0.43281 | 0.44926 | 0.45545 | 0.45755 | 0.45753 | 0.45753 | 0.45561 | 0.44745 | 0.44134 | 0.43114 | 0.42298 | 0.40867 | 0.39846 | 0.3862 | 0.36779 | 0.34325 | 0.32484 | 0.30028 | 0.27982 | 0.25322 | 0.2266 | 0.20409 | 0.17543 | 0.15291 | 0.12629 | 0.10377 | 0.075104 | 0.05053 | 0.019812 | -0.0047484 | -0.033414 | -0.060025 | -0.088688
= tip-speed ratio

## Slide 12: Air Density Adjustment
If the controller is not modified, a change in air density moves the TSR values.
Flat top => no change in Cp for small changes in density.
=> 1/3 power rule is valid.
Chart: Density=1.225
| 2.0169307999999999 | 2.2413694999999998 | 2.465808 | 2.7350501999999999 | 3.0939000000000001 | 3.2956150000000002 | 3.4523861 | 3.6091852000000002 | 3.7659563999999999 | 3.9003117 | 4.0346390000000003 | 4.1463823 | 4.2806259999999998 | 4.4373129999999996 | 4.5940285000000003 | 4.7508553999999998 | 4.9525703999999999 | 5.1991449999999997 | 5.4681635000000002 | 5.8269013999999997 | 6.1183075999999996 | 6.4996289999999997 | 6.9035343999999998 | 7.3074960000000004 | 7.6665979999999996 | 7.9583680000000001 | 8.2726100000000002 | 8.6318239999999999 | 9.0134530000000002 | 9.4175825 | 9.7767959999999992 | 10.158537000000001 | 10.472891000000001 | 10.832160999999999 | 11.213958 | 11.708059 | 12.112299999999999 | 12.494182 | 12.83112 | 13.235473000000001 | 13.594938000000001 | 13.931903999999999 | 14.246510000000001 | 14.561031 | 14.830721 | 15.122799000000001 | 15.414961 | 15.662179 | 15.954370000000001 | 16.313807000000001 | 16.628412000000001 | 16.987879 | 17.324928
Cp | 0.0038738 | 0.0038994 | 0.003925 | 0.010106 | 0.028598 | 0.049122 | 0.073741 | 0.09631 | 0.12093 | 0.1435 | 0.16811 | 0.20298 | 0.23374 | 0.26451 | 0.29323 | 0.31375 | 0.33428 | 0.35686 | 0.37944 | 0.40613 | 0.43281 | 0.44926 | 0.45545 | 0.45755 | 0.45753 | 0.45753 | 0.45561 | 0.44745 | 0.44134 | 0.43114 | 0.42298 | 0.40867 | 0.39846 | 0.3862 | 0.36779 | 0.34325 | 0.32484 | 0.30028 | 0.27982 | 0.25322 | 0.2266 | 0.20409 | 0.17543 | 0.15291 | 0.12629 | 0.10377 | 0.075104 | 0.05053 | 0.019812 | -0.0047484 | -0.033414 | -0.060025 | -0.088688
Chart: Density=1.2
| 2.0169307999999999 | 2.2413694999999998 | 2.465808 | 2.7350501999999999 | 3.0939000000000001 | 3.2956150000000002 | 3.4523861 | 3.6091852000000002 | 3.7659563999999999 | 3.9003117 | 4.0346390000000003 | 4.1463823 | 4.2806259999999998 | 4.4373129999999996 | 4.5940285000000003 | 4.7508553999999998 | 4.9525703999999999 | 5.1991449999999997 | 5.4681635000000002 | 5.8269013999999997 | 6.1183075999999996 | 6.4996289999999997 | 6.9035343999999998 | 7.3074960000000004 | 7.6665979999999996 | 7.9583680000000001 | 8.2726100000000002 | 8.6318239999999999 | 9.0134530000000002 | 9.4175825 | 9.7767959999999992 | 10.158537000000001 | 10.472891000000001 | 10.832160999999999 | 11.213958 | 11.708059 | 12.112299999999999 | 12.494182 | 12.83112 | 13.235473000000001 | 13.594938000000001 | 13.931903999999999 | 14.246510000000001 | 14.561031 | 14.830721 | 15.122799000000001 | 15.414961 | 15.662179 | 15.954370000000001 | 16.313807000000001 | 16.628412000000001 | 16.987879 | 17.324928
Cp | 0.0038738 | 0.0038994 | 0.003925 | 0.010106 | 0.028598 | 0.049122 | 0.073741 | 0.09631 | 0.12093 | 0.1435 | 0.16811 | 0.20298 | 0.23374 | 0.26451 | 0.29323 | 0.31375 | 0.33428 | 0.35686 | 0.37944 | 0.40613 | 0.43281 | 0.44926 | 0.45545 | 0.45755 | 0.45753 | 0.45753 | 0.45561 | 0.44745 | 0.44134 | 0.43114 | 0.42298 | 0.40867 | 0.39846 | 0.3862 | 0.36779 | 0.34325 | 0.32484 | 0.30028 | 0.27982 | 0.25322 | 0.2266 | 0.20409 | 0.17543 | 0.15291 | 0.12629 | 0.10377 | 0.075104 | 0.05053 | 0.019812 | -0.0047484 | -0.033414 | -0.060025 | -0.088688
Chart: Density=1.0
| 2.0169307999999999 | 2.2413694999999998 | 2.465808 | 2.7350501999999999 | 3.0939000000000001 | 3.2956150000000002 | 3.4523861 | 3.6091852000000002 | 3.7659563999999999 | 3.9003117 | 4.0346390000000003 | 4.1463823 | 4.2806259999999998 | 4.4373129999999996 | 4.5940285000000003 | 4.7508553999999998 | 4.9525703999999999 | 5.1991449999999997 | 5.4681635000000002 | 5.8269013999999997 | 6.1183075999999996 | 6.4996289999999997 | 6.9035343999999998 | 7.3074960000000004 | 7.6665979999999996 | 7.9583680000000001 | 8.2726100000000002 | 8.6318239999999999 | 9.0134530000000002 | 9.4175825 | 9.7767959999999992 | 10.158537000000001 | 10.472891000000001 | 10.832160999999999 | 11.213958 | 11.708059 | 12.112299999999999 | 12.494182 | 12.83112 | 13.235473000000001 | 13.594938000000001 | 13.931903999999999 | 14.246510000000001 | 14.561031 | 14.830721 | 15.122799000000001 | 15.414961 | 15.662179 | 15.954370000000001 | 16.313807000000001 | 16.628412000000001 | 16.987879 | 17.324928
Cp | 0.0038738 | 0.0038994 | 0.003925 | 0.010106 | 0.028598 | 0.049122 | 0.073741 | 0.09631 | 0.12093 | 0.1435 | 0.16811 | 0.20298 | 0.23374 | 0.26451 | 0.29323 | 0.31375 | 0.33428 | 0.35686 | 0.37944 | 0.40613 | 0.43281 | 0.44926 | 0.45545 | 0.45755 | 0.45753 | 0.45753 | 0.45561 | 0.44745 | 0.44134 | 0.43114 | 0.42298 | 0.40867 | 0.39846 | 0.3862 | 0.36779 | 0.34325 | 0.32484 | 0.30028 | 0.27982 | 0.25322 | 0.2266 | 0.20409 | 0.17543 | 0.15291 | 0.12629 | 0.10377 | 0.075104 | 0.05053 | 0.019812 | -0.0047484 | -0.033414 | -0.060025 | -0.088688
STALL!!
Large change in air density:
  => change in Cp
  Operates in stall at rated
1/3 power rule no longer valid
Controllers for high-altitude sites modified to correct TSR

## Slide 13: Air Density Adjustment
1/3 power rule should be implemented on TI=0 power curve.
  Due to large uncertainty in , may cause more problems than it solves.
Chart: Nordex 2.5MW – Adjusting from 1.225kg/m3 to 1kg/m3
| 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20
rho=1.225 | 34 | 88 | 155 | 237 | 333 | 448 | 582 | 738 | 919 | 1123 | 1351 | 1604 | 1845 | 2043 | 2200 | 2321 | 2409 | 2467 | 2495 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500
rho=1.0 | 22 | 66 | 121 | 188 | 267 | 359 | 467 | 594 | 740 | 906 | 1090 | 1293 | 1512 | 1746 | 1946 | 2110 | 2242 | 2344 | 2419 | 2469 | 2496 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500
Chart: Nordex 2.5MW – Adjusting from 1.225kg/m3 to 1kg/m3
| 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20
rho=1.225 | 34 | 88 | 155 | 237 | 333 | 448 | 582 | 738 | 919 | 1123 | 1351 | 1604 | 1845 | 2043 | 2200 | 2321 | 2409 | 2467 | 2495 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500
rho=1.0 | 22 | 66 | 121 | 188 | 267 | 359 | 467 | 594 | 740 | 906 | 1090 | 1293 | 1512 | 1746 | 1946 | 2110 | 2242 | 2344 | 2419 | 2469 | 2496 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500
IEC | 14.3 | 58.9 | 114.8 | 182.9 | 263.9 | 358.1 | 469.3 | 597.4 | 745.1 | 914.8 | 1104.7 | 1315.4 | 1550.4 | 1782 | 1980.4 | 2141.1 | 2268.6 | 2366.1 | 2436.1 | 2479.4 | 2497.2 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500
WakeBlaster | 17.1 | 62.7 | 119 | 187.6 | 267.3 | 362.6 | 473.5 | 602.5 | 752.3 | 920.8 | 1109.7 | 1326.1 | 1547.3 | 1757.1 | 1958.2 | 2140.2 | 2287.9 | 2392.9 | 2452.8 | 2477.3 | 2488.3 | 2494.1 | 2497.1 | 2498.6 | 2499.3 | 2499.7 | 2499.8 | 2499.9 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500
Svenningsen | 14.3 | 58.9 | 114.8 | 182.9 | 263.9 | 358.1 | 469.3 | 597.4 | 745.1 | 915 | 1086.4 | 1272.2 | 1475.6 | 1683 | 1873.1 | 2031.6 | 2161.8 | 2267.4 | 2350.8 | 2414.3 | 2460.4 | 2487.5 | 2498 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500

## Slide 14: Rotor Equivalent Wind Speed
Current practice based on :
BUT:
WakeBlaster calibration & validation shows linear average to be more representative:
is fixed for whole rotor
and rotor will operate at varying non-optimal angles of attack.
= rotor area
= aerodynamic torque
= rotor speed

## Slide 15: Any Questions?
philip.bradstock@proplanen.com
wakeblaster@proplanen.com